## Cost Summary
Improving access to clean drinking water for the urban poor in Peshawar, Pakistan (Lot 2 UV Filtration Plant)
Activity - 1.1.4 Clean drinking water supply systems developed/ rehabilitated in target location along with business models
Cost Summary for Ali colony Piraghaib Baba kachi Abadi-Changar Abad, Dalazak Road Peshawar, Near Railway Station
Sr # | Activity/work | Cost in PKR
2 | UV Filtration Plant Unit | 0
4 | Grand Total | 0
5 | Cost for 1 Unit Complete | 0
6 | Cost for 2 Units | 0

## UV Filtration Plant
Provision / Install Water Filtration Plant
P/Installation, Testing and Commissioning of Filtration Plant capacity of 2000 Liters per hour approved with all accessories and water supply system complete in all respect, to the entire satisfaction of Engineer In charge.
Activity | Water Filtration Plant | P/Installation, Testing and Commissioning of Filtration Plant capacity of 2000 Liters per hour filtration System, Complete in all Respect, Contractor will ensure & Provide Post Installation Water Quality Test from Pakistan Council of Research in Water Resources (PCRWR) , |  | 1 | Nos |  |  | 0
Contractor is duly responsible to Ensure Water Quality as safe & hygiene drinking water. Plant is subjected to the approval of concerned Engineer at site.
Total Amount | [7 empty] | 0
Detailed Specification of UV Plant
Sr. No | Description |  | Specifications |  |  | Make/Size | Qty.
1 | Low pressure feed pump CNP new |  | Make: Felsom or CNP/ Italy(Ref) | Material: SS304/SS316 | Model: 70 psi Max. 2hp | 1 hp | 1
|  |  | Capacity: 12 m3/h | Discharge Pressure: 4 bar | Type: Centrifugal
2 | Vessel for Multimedia Filter |  | Size: 16"*65" | Backwash: 3-way valve manual 1" | Media: Hi-Silica Gravel Sand | 16"*65" | 1
3 | Vessel for activated carbon filter |  | Size: 16"*65" | Backwash: 3-way valve manual 1" | Media: Granula Activated Carbon | 16*65 | 1
4 | Multiple 3 Way |  |  |  |  | 1" | 2
5 | Housing + Catridge PPF |  | Size: 20" | PPF Jumbo | 5 micron | J-20"-5 | 1
6 | Housing + Catridge PPY |  | Size: 20" | PPY Jumbo | 1 micron | J-20"-1 | 1
7 | Pressure Guages + Switches |  | Stainless Steel low and high pressure guages | 2.5" dia | Material: SS316 | 2.5" | 2
8 | Online TDS meter |  | Make: Create / Kamatsu | Location: Permeate Line | Range: 0-1000 us/cm or 0-2000 us/cm | China or best quality possible | 1
9 | Control panel |  | Indoor Installation with front access | Material: MS | Local made | Best Quality Possible | 1
10 | UV Lamps + Panels |  | Lamp: Philips (Poland) or Atlantic | Quartz: Aqua Guard | Chamber: Local (Double) Panel: MS powder coated | 33" Philips or Atlantic made | 2
11 | Fitting UPVC |  | Material: UPVC | Era, Taiwan | Size: 1" | Era | 1
12 | Sand Media |  | Model of Vessel: 16" * 65" | Material: Fiber Reinforced Plastic | Design Pressure: 150 Psi | Best Quality Possible | 200KG
|  |  | Make of Vessel: Pentair | Operation: Manual | Type of Control Valve: Side Mounted
|  |  | Make of Valve: Imported | Filling media: Gravel, Sand etc | Piping: UPVC
13 | Carbon |  | Model of Vessel: 16" * 65" | Material: Fiber Reinforced Plastic | Design Pressure: 150 Psi | Holland, Canada Coconut Shell made | 25KG
|  |  | Make of Vessel: Pentair | Operation: Manual | Type of Control Valve: Side Mounted
|  |  | Make of Valve: Imported | Filling Media: Activated Carbon | Piping: UPVC
14 | Jumbo Housing |  |  |  |  | Taiwan | 2
15 | 500 Gallon Storage Tank with float switches |  |  |  |  | Local | 1
16 | MS Skid Frame |  |  |  |  | Mild steel | 1