## Summary
Construction & Installation of Solar Based Drinking Water Supply System
Village Safi Abad, UC Jalozai, District Nowshehra
Summary Of Cost
S.No | Description | Amount (PKR)
1 | A.Drilling and Development of Borehole:
2 | B.Supply and Installation of Solar Based Pumping Unit
3 | C.Sanitary & Fittings
4 | D.Construction of Communal Water Tanks (3,000 gallons)
5 | E.Scheme Visibility
Total Cost of Water System (PKR)
Improving Living conditions and Resilience of Afghan Refugees and Host Communities in, Khyber Pakhtunkhwa, Pakistan.

## Budget
Construction & Installation of Solar Based Drinking Water Supply System
Village Safi Abad, UC Jalozai, District Nowshehra
Abstract Of Cost
1 | A.Drilling and Development of Borehole:
S/N | Activities | Unit | Quantity | Unit Rate | Total Cost
|  |  |  | PKR | PKR
1 | Drilling of bore holes in all types of soils including sinking and withdrawing of pipe and collection of 100 % corings, complete as per specifications: Dia of Borehole 8" i/d | Rft | 240
2 | Providing & Installation of UPVC Class-C blind pipe including lowering, jointing and fixing with 6" overlapping at joints complete: 6" Nominal Pipe Size (NPS) (150 mm) | Rft | 201
3 | Providing & Installation of UPVC class-C strainer pipe including lowering, jointing with 6" overlapping at joints complete: 6" Nominal Pipe Size (NPS) (150 mm) | Rft | 39
4 | Providing and installing wooden bail plug for 6" Nominal Pipe size: | Each | 1
5 | Providing & fixing filter cloth with cobler thread for UPVC filter pipe: (length 39 feet, diameter 6"). | Job | 1
6 | Supply and placing Shrouding materials with graded pack gravel 3/8" (10 mm) to 1/8" (3 mm) around the in bore hole complete as per specification:- | Rft | 80
7 | Testing and development of borehole till reaching clear water. | Job | 1
Sub Total (PKR)
2 | B.Supply and Installation of Solar Based Pumping Unit
1 | Supply, Installation, testing and commissioning of Submersible Pump (ISO - 9906 and PSQCA Certified) coupled with submersible rewind-able Electric Motor with AC winding, designed for efficient operation at 220-240V single-phase or 380-415V three-phase voltage including all accessories like Motor Control Unit (equipped with UV/OV, dry run protection device, surge protection, phase reverse indicator), suspension clamps, steel rope 10 mm, cable ties, starter board etc. and all other required components. Complete in all respect (Size 2.5 HP or Equivalent , capable to deliver water @ 17 GPM against the TDH 270 feet) - 6 months warranty | Job | 1
2 | Supply and installation of Submersible Flat Cable made of 99.9% copper, coated with double PVC asper BSS Standards, 2x10mm2 or suitable size capable to safly operate the proposed pumping unit. | Rft | 300
3 | Supply and installation of high-efficiency solar panels (A grade, Bifacial, N type) rated for reliable energy production. The panels ‎should be from reputable manufacturers and latest technology. Each panel should have below specs:‎ • 21-23% efficiency with maximum power output.‎ • Weather-resistant with high-grade aluminum frames and double glass, designed ‎to withstand harsh environmental conditions (hail, wind and snow loads).‎ • Should have certificates IEC 61215, IEC 61730 and PID etc.‎ • Documented and verifiable to prove the country of origin and the manufacturer’s details. •(25 Years linear performance warranty & 12 Years product warranty)‎ | Watts | 3500
4 | Provision made for supply and erecting of Pole mounted/customized frame for the proposed solar array power (watts). The pole should be made of HDG steel having 6 feet high from ground level and an adjustable tilt angle up to 35 degrees. The pole should have 6 inch diameter GI pipe properly embedded in a concrete foundation (Size: 12" x 12" x 30"). The top frame for fixing solar panels should be made of MS angle iron or rectangular tube with SS fasteners and aluminum clamps. The mount structure should withstand wind speeds up to 150 km/h and should be corrosion resistant duly painted and made with 14 SWG (complete in all respect). | Job | 1
4 | Supply, installation, testing, and commissioning of VFD Inverter suitable for proposed pumping unit ( 3.5 KW or above to 4.2 KW), designed to provide efficient and smooth operation and have compatibility with proposed solar array. The VFD must be ISO-certified and documented & verifiable and should have compliance with national & international standards (with 1-year warranty). The rate should be inclusive of all required items (safety breakers, MCU, main switch, volt meter and GI safety box etc) complete installation in all repect. | Job | 1
5 | Provision made for supply and erecting the safety box for VFD made of MS sheet 16 SWG, duly painted designed to place/install the VFD in outdoor conditions. The box should be lockable and have perforations in sides for ventilation purposes. the box should be mounted on a pipe having 2 inch diameter made of mild steel, fixed at 3 feet from ground level and embedded in (12" x 12" x 18") concrete foundation. The box should have door (open outward side) with locking arrangements and cable entry points. (size of box: 3.5x2.5x1.25 feet). as per the attached drawing | Job | 1
6 | Provision made for the electrical wiring & required accessories for the installation of solar panels, VFD/inverter and control panels. The work includes wiring from the solar panel array to the inverter, panel wiring and conduit installation using high-quality materials and appropriate sizes. | Job | 1
Sub Total (PKR)
3 | C.Sanitary & Fittings
S/N | Activities | Unit | Quantity | Unit Rate | Total Cost
|  |  |  | PKR | PKR
1 | Providing & Installation of PVC 3" dia, class B pipe including all specials & accessories for drainage | Rft | 30
2 | Providing and Fixing Brass gate valve heavy duty, 2" dia including all specials & accessories complete in all respect | No | 2
3 | Provision made for construction of valve chamber having internal size (3x3x2 feet). The chamber should be constructed with brick masonry (9 inches thick) using 1:5 CSM and PCC 1:3:6 with 4 inches thickness should be provided in bed. The brick work should be duly plastered from both sides and a cover made of angle iron and MS sheet (18 SWG) having locking arrangement should be fixed on top. As per the drawing. | Job | 1
4 | Provision made for construction of chamber for the protection of borehole having internal size (2x2x2.5 feet). The chamber should be constructed with brick masonry (9 inches thick) using 1:5 CSM and PCC 1:3:6 with 4 inches thickness should be provided in bed. The brick work should be duly plastered from both sides and a cover made of angle iron and MS sheet (18 SWG) having locking arrangement should be fixed on top. As per the drawing. | Job | 1
5 | Providing and fixing chromium plated (CP) bib cock, heavy duty of approved quality including all specials and accessories for installation in water tank : (Size: 1/2") | Each | 4
6 | Providing, laying, cutting, jointing, testing and disinfecting High Density Polyethylene Pipe (HDPE), including all specials and accessories complete in all respects and properly burried up to 1 feet depth and backfilling (50 mm) PN-12.5 | Rft | 350
7 | Provision made for construction of soakage pit (conical type) having 2 feet diameter at bottom and 4 feet at top with 4 feet total depth. The pit should be filled with filter well graded filter media: as per the drawing | Job | 1
8 | Floor Trape made of Stainless steel having 6 inches dia - Heavy Duty | Each | 1
Total Cost of Sanitary Fittings
4 | D.Construction of Communal Water Tanks (3,000 gallons)
S/N | Activities | Unit | Quantity | Unit Rate | Total Cost
|  |  |  | PKR | PKR
1 | Excavation in foundation for water tank in any soil. | Cft | 263.5
2 | Plain Cement Concrete including placing, compacting, finishing & curing Ratio: 1:4:8 | Cft | 28.25
3 | Coursed rubble masonry in foundation and plinth using CSM ratio 1:6. The stones should be dressed with hammer to make regular shape and size. The masonry should be carried out with good workmanship to make uniform courses with aligned vertical and horizontal joints to maintain proper bond. Proper packing with smaller stones and mortar should be ensured to fill voids having no honeycombing. The outer surface should be dressed and well aligned to provide smooth & uniform face suitable for plastering/pointing. | Cft | 190.6875
4 | Providing & laying stone soling in water logged area including granular filling, watering & compaction complete. | Cft | 89.25
5 | Plain Cement Concrete including placing, compacting, finishing & curing Ratio: 1:4:8 | Cft | 51.75
6 | 1st class brick work with Cement, sand mortar 1:3 | Cft | 184.5
7 | R.C.C as in Base Slab, core wall & Roof slab (1:2:4) included cost of shuttering complete with all respect. | Cft | 230.3958
8 | Supply & fabricate M.S. reinforcement for cement concrete (Hot rolled deformed bars Grade 40) | Kg | 512.2082
9 | Cement plaster with CSM 1:3, ¾ inches thick, using zero-gauge chips applied on the internal surfaces of the water tank. A suitable waterproofing chemical admixture should be added to the mortar to ensure prevention of leakage & seepage. | Sft | 204
10 | Cement plaster with CSM 1:4, 1/2 inches thick on external surface of water tank. | Sft | 76.6667
11 | Plain Cement Concrete including placing, compacting, finishing & curing Ratio: 1:2:4 | Cft | 66.4375
12 | F/instalation of m.s main hole cover 2'x2' (18 SWG), using 1.5"x1.5"x.25" angle iron frame duly painted with lock arrangement complete | Each | 1
13 | P/Instalation of 2" dia G.I (E.L) Pipe for wash out and ventilation including all the accessories as per the drawing complete in all respect. | Rft | 6
14 | P/Instalation of 2" dia G.I (E.L) Pipe for inlet and overflow including all the accessories as per the drawing complete in all respect. | Rft | 20
15 | Preparing surface & painting with weathershield paint . (2 coats) | Sft | 288
16 | Erection and removal of Steel Form work with smooth and aligned Surface Finshing for RCC core walls in water tank | Sft | 204
17 | Cement pointing (struck type) on external Brick masonry walls: Ratio 1:4 | Sft | 264
18 | Cement pointing (Ribbon type) on external stone masonry walls in plinth using CSM 1:4 including raking, cleaning and watering the joints. The mortar should be pressed into the joints and uniform raised ribbon should be formed. The surface should be neatly finished and extra mortar be removed to ensure esthetic look. | Sft | 48
Cost of Single Water Tank
5 | E.Scheme Visibility
1 | Provision made for making art work / wall chalking on walls of water tank including logos/images/ writing message with paint. The paint should be UV-resistant, waterproof and long lasting finish against environmental factors. The height, spacing and letter size for both painting logos and writing message should ensure professional look, clear visibility and background colour using stencils. (Set: 2 logos each of 24 x 24 inches and write up maximum 3 to 4 lines) | Set | 1
2 | Providing and installation of Sign Board (4'x3') with standard text made of MS sheet (18 SWG) fixed/welded with 02 MS pipe having 4 feet height & 1.5" dia for verticle support properly embeded in PCC to withstand against high speed winds. | NSI | 1
Cost of Visibility
Improving Living conditions and Resilience of Afghan Refugees and Host Communities in, Khyber Pakhtunkhwa, Pakistan.

## Sanitary & Fitting
Sanitary & Fitting Items
S/N | Activities | Unit | Quantity
1 | Providing & Installation of PVC 3" dia pipe including all specials & accessories for drainage | Rft | 30
2 | Supply and installation of Gate Valves 1.5" including all specials & accessories complete in all respect | No | 4
3 | 1.5'X1.5' door (Borehole cap), made of 18 SWG sheet and angle iron frame 1"x1" duly painted and locakble arrangements: comple in all recpect | Job | 1
4 | Provision made for construction of valve chamber having internal size (2x2x2 feet). The chamber should be constructed with brick masonry (9 inches thick) using 1:5 CSM and PCC 1:3:6 with 4 inches thickness should be provided in bed. The brick work should be duly plastered from both sides and a cover made of angle iron and MS sheet (18 SWG) having locking arrangement should be fixed on top. As per the drawing. | Job | 1
5 | Provision made for construction of chamber for the protection of borehole having internal size (2x2x2.5 feet). The chamber should be constructed with brick masonry (9 inches thick) using 1:5 CSM and PCC 1:3:6 with 4 inches thickness should be provided in bed. The brick work should be duly plastered from both sides and a cover made of angle iron and MS sheet (18 SWG) having locking arrangement should be fixed on top. As per the drawing. | Job | 1
6 | Bib cocks, CP | Each | 4
7 | HDPE pipe, PN 12.5 with 40 mm i/d | Rft | 350
8 | Floor trape for waste water made of SS steel with 6 inches dia - Heavy Duty | No | 1

## Storage Tank - 3K gallons
Construction of 3K-Gallons Surface Tank
Backup Calculations
S/N0 | Description | NO | Length (ft) | Width (ft) | Height / Depth(ft) | Quantity | Unit
1 | Excavation
1.1 | water tank foundation
1.2 | Long wall | 2 | 13.5 | 2 | 1.5 | 81
1.3 | Partition wall | 1 | 10.5 | 2 | 1.5 | 31.5
1.4 | Short wall | 2 | 9.5 | 2 | 1.5 | 57
1.5 | Drain under bib cocks | 1 | 8 | 1.75 | 0.5 | 7
1.6 | Sanitary Seal | 1 | 3 | 3 | 3 | 27
1.7 | for drain pipe | 2 | 30 | 1 | 1 | 60
| Total Quantity for excavation |  |  |  |  | 263.5 | Cft
2 | PCC 1:4:8 in foundation
2.1 | Long wall | 2 | 13.5 | 2 | 0.25 | 13.5
2.2 | Short wall | 2 | 9.5 | 2 | 0.25 | 9.5
2.3 | Partition wall | 1 | 10.5 | 2 | 0.25 | 5.25
| Total Quantity for PCC 1:4:8 |  |  |  |  | 28.25 | Cft
3 | Stone masonry in foundation & plinth
3.1 | Long wall | 2 | 13.5 | 1.5 | 2.25 | 91.125
3.2 | Short wall | 2 | 9.5 | 1.5 | 2.25 | 64.125
3.2 | Partition wall | 1 | 10.5 | 1.5 | 2.25 | 35.4375
| Total Quantity for Stone masonry |  |  |  |  | 190.6875 | Cft
4 | Providing & laying stone soling in water logged area including granular filling & compaction complete.
4.1 |  | 1 | 10.5 | 8.5 | 1 | 89.25
| Total Quantity for Filling |  |  |  |  | 89.25 | Cft
5 | PCC 1:4:8 in base
5.1 |  | 1 | 13.5 | 11.5 | 0.33333 | 51.75
| Total Quantity for PCC 1:4:8 |  |  |  |  | 51.75 | Cft
6 | BBM in water tank (1:3)
6.1 | Wall 9" Thick
| Long wall | 2 | 12.5 | 0.75 | 6 | 112.5
| Short wall | 2 | 8 | 0.75 | 6 | 72
| Total Quantity for BBM |  |  |  |  | 184.5 | Cft
7 | R.C.C as in Base Slab & Roof slab (1:2:4)
7.1 | W/Tank Base slab | 1 | 12.5 | 9.5 | 0.5 | 59.375
7.2 | W/Tank Roof slab | 1 | 13.5 | 11.5 | 0.41667 | 64.6875
7.3 | Core wall long side | 2 | 11 | 0.5 | 6 | 66
7.4 | Core wall short side | 2 | 7 | 0.5 | 6 | 42
| D/d Main hole quantity | 1 | 2 | 2 | 0.41667 | 1.6667
| Total Quantity for RCC 1:2:4 |  |  |  |  | 230.3958 | Cft
8 | Fibrication of mild steel reinforcement for R.C.C Work @ 1% of the concrete volume
[6 empty] | 512.2082 | kg
| Total Quantity for steel |  |  |  |  | 512.2082 | kg
9 | P.C Plaster in (1:3) water tank internal
Inside W/Tank
| Long wall | 2 | 10 |  | 6 | 120
| Short wall | 2 | 7 |  | 6 | 84
| Total Quantity for internal plaster |  |  |  |  | 204 | Sft
10 | Plaster on external side
| Strips on concrete layers in base external side | 1 | 46 |  | 0.83333 | 38.3333
| Strips on BM under slab | 1 | 44 |  | 0.41667 | 18.3333
| Strips on corner | 4 | 0.83333 |  | 6 | 20
| Total Quantity for plaster |  |  |  |  | 76.6667 | Sft
11 | Construction of drain, platform and pads with PCC 1:2:4
| side walls of drain under bib cocks (tank side) | 2 | 12.5 | 0.5 | 0.5 | 6.25
| Drain floor | 1 | 12.5 | 1.75 | 0.5 | 10.9375
| wall on both ends of drain | 2 | 0.75 | 0.5 | 0.5 | 0.375
| Platform | 1 | 9.5 | 2.5 | 0.5 | 11.875
| Sanitary Seal | 1 | 3 | 3 | 3 | 27
| Fillet in water tank | 4 | 0.5 | 0.5 | 6 | 6
| Seating pads | 4 | 1 | 1 | 1 | 4
| Total Quantity for PCC 1:2:4 |  |  |  |  | 66.4375 | Cft
12 | MS Main hole cover 2'x2' with lock arrangement | 1 |  |  |  | 1 | each
13 | F/Instalation of 1.5" dia G.I Pipe for over flow, Inlet | 1 |  |  |  | 20 | rft
14 | F/Instalation o f 2" dia G.I Pipe for wash out & ventilation |  |  |  |  | 6 | rft
15 | weather shield on external walls all around
| Long walls | 2 | 12.5 |  | 6 | 150
| Short walls | 2 | 9.5 |  | 6 | 114
| Shades | 1 | 48 |  | 0.5 | 24
| Total Quantity for weather shield |  |  |  |  | 288 | Sft
16 | Pointing Out side on water tank (struck) | 1 | 44 |  | 6 | 264 | sft
17 | Pointing Out side on stone masonry in plinth (ribbon) | 1 | 48 |  | 1 | 48 | sft
18 | Form work form RCC | 1 | 34 |  | 6 | 204 | sft