## Design Calculation
Name of water Supply Scheme: | DWSS Safi Abad
Location Reference: | UC Jalozai, District Nowshera
Daily Demand Calculation
Total No of House Holds (Current) |  | 88 |  |  |  | TDH
Size of House Holds |  | 8.3 |  |  |  | Total Head = |  | Suction+Delivery+Losses
Total Population of H.Hs |  | 730.4 |  |  |  | Suction Head | Hs(ft) | 210
P(N) = P(1 + n /100)N | N= Years, n = growth rate, P= Population |  |  | Design Period | 5 Years | Delivery Head | Hd(ft) | 20
Population in 5 years with 3 % growth rate per year |  | 846.7338 | Future population after 5 years |  |  | Friction Losses | Hf(ft) | 35
Demand per capita/day |  | 25 | Litres | 6.605 | US gallons | Total Head | H(ft) | 265
Demand of Population per day |  | 21168.3446 | Litres | 5592.6934 | US gallons
Required Storage per day |  | 5592.6934 | US gallons | 21.1683 | m3 | Daily water Demand per capita per day
Wasteage and Peak hours demand @10% |  | 559.2693 | US gallons | 2.1168 | m3 | Purpose | Quantity (LPCD)
Net water demand per day |  | 6151.9628 | US gallons | 23.2852 | m3 | Drinking | 3
Half day required storage (The pumping unit will be capable to fill the storage two times) |  | 3075.9814 | US gallons | 11.6426 | m3 | Basic hygiene | 3
Required Discharge (Flow rate) @ 6 hours pumping per day |  | 1025.3271 | Gallons/hour (GPH) | 17.0888 | Gallons/minute (GPM) | Cooking | 3
Pump Selection to deliver the required discharge against the TDH | [5 empty] | Religious activity | 8
Horse Power (BHP) | Q x TDH x S.G |  |  | Specific Gravity for water = | 1 | Toilet | 4
| 3960 x Ep |  |  | Pump efficiency (Ep) = | 60% - 70% | Livestock | 4
Pump required (BHP) | 1.9059 |  |  | Q | GPM | Total | 25
Say | 2.5
Solar Power Selection for Proposed Pumping Unit
Proposed pump | 2.5 | HP | 1 HP = 746 Watts
Power required for the pump | 1865 | Watts
Add FOS @ 25% | 466.25 | Watts | FOS ranges 10% to 25%
Add Solar panel loses @ 30% | 559.5 | Watts | Panel loses ranges from 22% to 30%
Total Solar Power required | 2890.75 | Watts
Say | 3500 | Watts | For more Efficiency