## Design Calculation
Name of water Supply Scheme: | DWSS Sarrai kamar
Location Reference: | UC Jalozai, District Nowshehra
Daily Demand Calculation
Total No of House Holds (Current) |  | 172 |  |  |  | TDH
Size of House Holds |  | 8.3 |  |  |  | Total Head = |  | Suction+Delivery+Losses
Total Population of H.Hs |  | 1427.6 |  |  |  | Suction Head | Hs(ft) | 240
P(N) = P(1 + n /100)N | N= Years, n = growth rate, P= Population |  |  | Design Period | 5 Years | Delivery Head | Hd(ft) | 20
Population in 5 years with 3 % growth rate per year |  | 1654.9797 | Future population after 5 years |  |  | Friction Losses | Hf(ft) | 35
Demand per capita/day |  | 25 | Litres | 6.605 | US gallons | Total Head | H(ft) | 295
Demand of Population per day |  | 41374.4917 | Litres | 10931.1735 | US gallons
Required Storage per day |  | 10931.1735 | US gallons | 41.3745 | m3 | Daily water Demand per capita per day
Wasteage and Peak hours demand @10% |  | 1093.1174 | US gallons | 4.1374 | m3 | Purpose | Quantity (LPCD)
Net water demand per day |  | 12024.2909 | US gallons | 45.5119 | m3 | Drinking | 3
one third (1/3) required storage (The pumping unit will be capable to fill the storage three times) |  | 4008.097 | US gallons | 22.756 | m3 | Basic hygiene | 3
Required Discharge (Flow rate) @ 6 hours pumping per day |  | 2004.0485 | Gallons/hour (GPH) | 33.4008 | Gallons/minute (GPM) | Cooking | 3
Pump Selection to deliver the required dischage against the TDH | [5 empty] | Religious activity | 8
Horse Power (BHP) | Q x TDH x S.G |  |  | Specific Gravity for water = | 1 | Toilet | 4
| 3960 x Ep |  |  | Pump efficiency (Ep) = | 60% - 70% | Livestock | 4
Pump required (BHP) | 2.9273 |  |  | Q | GPM | Total | 25
Say | 3
Solar Power Selection for Proposed Pumping Unit
Proposed pump | 3 | HP | 1 HP = 746 Watts
Power required for the pump | 2238 | Watts
Add FOS @ 25% | 447.6 | Watts | FOS ranges 10% to 25%
Add Solar panel losess @ 30% | 559.5 | Watts | Panel losess ranges from 22% to 30%
Total Solar Power required | 3245.1 | Watts
Say | 4000 | Watts